## README
This excel-tool is a translation based on the German document Netzverlustberechnung_Wärmedurchgangskoeffizient.xls which was developed by the Austrian "klimaaktiv QM Heizwerke" program.
Link to Netzverlustberechnung_Wärmedurchgangskoeffizient.xls
The translation was carried out within the European project ENhancing renewable heaT planning for improving the aiR quAlity of commuNities (ENTRAIN).
Please contact Sabrina Metz at s.metz@aee.at for any suggestion or bug-report of this tool.
"klimaaktiv QM Heizwerke" is a quality management program throughout Austria in order to improve the technical quality and efficiency of biomass heating plants and district heating grids. This is achieved by accompanying quality control during the planning, construction and operation phase. For consulting and further information see www.klimaaktiv.at/qmheizwerke
"klimaaktiv QM Heizwerke" is supported by the Austrian Federal Ministry for Climate Protection, Environment, Energy, Mobility, Innovation and Technology (BMK).

## Explanatory notes
This is a simplified calculation of the heat losses of a district heating networks based on static parameters (maximum heat losses at the design operating point). The aim is to calculate a key figure for a district heating network which allows to compared the relative heat losses (in percent) with other district heating networks. Thus, the calculated relative heat losses are always related to a year round operation. The heat losses (absolut value in MWh) related to the defined operating hours are calculated as well.
Step | Explanation
1 | All details must be entered on the "DHN heat losses" sheet, to the right there are hints on the necessary details.
2 | Enter the heating plant name and identification number so that the heating plant can be identified without misunderstanding.
3 | Enter the manufacturer's name of the pipe used, pipe type and type number or type designation.
4 | Enter the annual operating time of the district heating network in hours.
5 | Enter the supply temperature of the district heating network at the design operating point.
6 | Enter the return temperature of the district heating network at the design operating point.
7 | Average annual temperature of the pipe's surrounding soil.
8 | Annual heat sale according to the customer survey (i.e. expected to be sold). The heat losses of the district heating network will be later added to this value to determine the amount of heat fed into the DHN (see step 26).
10 | Pipe dimension: Introduce the nominal diameter, i.e. DN <X>. For two different pipe types (e.g. steel and plastic) of the same size, record these separately.
11 | Pipe lengths in meters ATTENTION: Enter supply and return pipe length.
13 | Specify heat transfer coefficient for the selected pipe type and dimensions according to the manufacturer's data sheet. This value will be later used (see step 14) to calculate the thermal power losses for the specified length, supply and return temperatures at the design operating point and soil temperature.
14 | The thermal power losses are calculated for each pipe entry based on the pipe length, the heat transfer coefficient, the supply and return temperature at the desing operating point and the surrounding/soil temperature. If the selected manufacturer uses a different calculation method, the heat transfer coefficients must be adjusted or the calculation formula must be changed.
15 | The reference annual heat losses in kWh/a are calculated from the thermal power losses and the annual number of operating hours of 8.760.
16 | Sum of column values. I.e. total ... pipe length, thermal power loss and reference annual heat losses.
Results:
20 | Net length in trench metres - A parallel laying of supply and return pipes is assumed. Thus, it corresponds to half of the figure given under (11).
21 | Net length in meters - sum of the columns values in (11). Assuming a parallel laying of supply and return pipes, it corresponds to twice the value of (20)
22 | Temperature difference of the network at the design operating point in °C - is calculated from (5) and (6).
23 | Thermal power losses of the district heating network in kW at the design operating point.
24 | Annual heat loss in MWh for the specified number of operating hours - based on the currently planned operating mode. If the network is only operated in winter, then the actual annual heat losses are the heat losses of the winter season and thus lower than the reference value (25).
25 | Reference annual heat losses in MWh. The value is calculated assuming that the district heating network is operated over the entire year at the design operating point. It serves to obtain comparable result figures for networks.
26 | Total annual heat feed into the district heating network. It corresponds to the sum of the annual heat sale and the reference value for the annual heat losses of the DHN
27 | Percentage reference value for the district heating network heat losses (reative losses) using the total amount of heat fed into the grid (step 26) as a reference.
30 | The data sheets of the pipe manufacturer must be attached to the PDF printout of this sheet!

## DHN heat losses
Simplified (static) calculation of heat losses in the district heating network (DHN)
(maximum heat loss at the design operating point)
from heat transfer coefficient [W/(m.K)]
Input cell:
Hints:
Author:
2 |  | Project designation, Proj. no.: |  |  |  | Heating plant designation and identification number
3 |  | Type of pipe used: |  |  |  | Manufacturer, type, type number etc.
4 |  | Operating hours: |  | h |  | Year round operation (8.760 h) or seasonal only;
5 |  | Supply temperature: |  | °C |  | Design data (based on heating plant design)
6 |  | Return temperature: |  | °C |  | Design data (based on heating plant design)
7 |  | Soil temperature: |  | °C |  | Present soil temperature (8°C / 10°C)
8 |  | Annual heat sale: |  | MWh
| Pipe dimension | Pipe length | Heat transfer coefficent | Thermal power loss | Reference annual heat losses
| [Text] | [m] | [W/(m.K)] | [kW] | [kWh/a]
| 10 | 11 | 13 | 14 | 15
| DN 20 | 0 | 0 | 0 | 0 | Specify pipe types with the corresponding lengths individually.
| DN 25 | 0 | 0 | 0 | 0 | Specific pipe heat losses
| DN 32 | 0 | 0 | 0 | 0 | If different pipe types of the same dimension are used (e.g. DN 50 steel and DN 50 plastic), list them separately.
| DN 40 | 0 | 0 | 0 | 0
| DN 50 | 0 | 0 | 0 | 0
| DN 65 | 0 | 0 | 0 | 0
| DN 80 | 0 | 0 | 0 | 0
| DN 100 | 0 | 0 | 0 | 0
| DN 125 | 0 | 0 | 0 | 0
| DN 150 | 0 | 0 | 0 | 0
| DN 200 | 0 | 0 | 0 | 0
| DN 250 | 0 | 0 | 0 | 0
| DN 300 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
16 | Sum: | 0 |  | 0 | 0
Results:
20 |  |  | Network-Trench : | 0 | m | I.e. trench length if supply and return pipes are always parallel to each other
21 |  |  | Network piping length : | 0 | m
22 |  |  | Temperature difference : | 0 | °C | Calculated based on design temperatures, i.e. supply temperature (step 5) and return temperature (step 6)
23 |  |  | Thermal power loss of the DHN : | 0 | kW | Heat losses in kW based on the network layout (total pipe length), heat transfer coefficient, average network temperatures at the design operating point and soil temperature
24 | Annual heat losses (based on the defined operating conditions/hours) : |  |  | 0 | MWh | Annual heat losses based on the defined (in step 4) operating hours
25 |  |  | Maximal heat losses (reference value) : | 0 | MWh | Reference annual heat losses of the district heating network (maximum value) assuming year-round operation (8.760 h) at the design operating point.
26 |  |  | Annual heat sale incl. DHN heat losses : | 0 | MWh | Total annual heat quantity required by the district heating network assuming year-round operation at design operating point.
27 |  |  | Percentage of DHN heat losses : | 0 | % | Relative heat losses; reference value for DHN heat loss assuming all year round operation
30 | Attach manufacturers data sheets of all used pipe types for this calculation!
Note on C15: Attention! Consider the supply AND return pipes!
Note on D15: Heat transfer coefficient for the pipes (supply and return) in Watt per Kelvin and meter of pipe length.
Note on F15: Reference (maximal) heat losses for year-round operation (8760h) at design operating point

## Example
Simplified (static) calculation of heat losses in the district heating network (DHN)
(maximum heat loss at the design operating point) | [5 empty] | (e.g. Kelit, Logstor)
from heat transfer coefficient [W/(m.K)]
| Exemplary calculation |  |  |  | Input cell:
Hints:
|  | Author: | Mrs. Smith
2 |  | Project designation, Proj. no.: | Example project |  |  |  | Heating plant designation and identification number
3 |  | Type of pipe used: | DH pipeType Plus, 2x |  |  |  | Manufacturer, type, type number etc.
4 |  | Operating hours: | 8760 | h |  |  | Year round operation (8.760 h) or seasonal only;
5 |  | Supply temperature: | 90 | °C |  |  | Design data (based on heating plant design)
6 |  | Return temperature: | 55 | °C |  |  | Design data (based on heating plant design)
7 |  | Soil temperature: | 10 | °C |  |  | Present soil temperature (8°C / 10°C)
8 |  | Annual heat sale: | 6250 | MWh
| Pipe dimension | Pipe length | Heat transfer coefficent | Thermal power loss | Reference annual heat losses
| [Text] | [m] | [W/(m.K)] | [kW] | [kWh/a]
| 10 | 11 | 13 | 14 | 15
| DN 20 | 816 | 0.1074 | 5.4774 | 47982.024 |  | Specify pipe types with the corresponding lengths individually.
| DN 25 | 396 | 0.1249 | 3.0913 | 27079.569 |  | Specific pipe heat losses
| DN 32 | 920 | 0.1362 | 7.8315 | 68603.94 |  | If different pipe types of the same dimension are used (e.g. DN 50 steel and DN 50 plastic), list them separately.
| DN 40 | 1208 | 0.1518 | 11.4609 | 100397.484
| DN 50 | 644 | 0.1644 | 6.6171 | 57965.796
| DN 65 | 176 | 0.1844 | 2.0284 | 17768.784
| DN 80 | 584 | 0.197 | 7.1905 | 62988.78
| DN 100 | 456 | 0.2037 | 5.8055 | 50855.742
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
16 | Sum: | 5200 |  | 49.5025 | 433642.119
Results:
20 |  |  | Network-Trench : | 2600 | m |  | I.e. trench length if supply and return pipes are always parallel to each other
21 |  |  | Network piping length : | 5200 | m
22 |  |  | Temperature difference : | 35 | °C |  | Calculated based on design temperatures, i.e. supply temperature (step 5) and return temperature (step 6)
23 |  |  | Thermal power loss of the DHN : | 49.5025 | kW |  | Heat losses in kW based on the network layout (total pipe length), heat transfer coefficient, average network temperatures at the design operating point and soil temperature
24 | Annual heat losses (based on the defined operating conditions/hours) : |  |  | 433.6421 | MWh |  | Annual heat losses based on the defined (in step 4) operating hours
25 |  |  | Maximal heat losses (reference value) : | 433.6421 | MWh |  | Reference annual heat losses of the district heating network (maximum value) assuming year-round operation (8.760 h) at the design operating point.
26 |  |  | Annual heat sale incl. DHN heat losses : | 6683.6421 | MWh |  | Total annual heat quantity required by the district heating network assuming year-round operation at design operating point.
27 |  |  | Percentage of DHN heat losses : | 6.4881 | % |  | Relative heat losses; reference value for DHN heat loss assuming all year round operation
30 | Attach manufacturers data sheets of all used pipe types for this calculation!
Note on C15: Attention! Consider the supply AND return pipes!
Note on D15: Heat transfer coefficient for the pipes (supply and return) in Watt per Kelvin and meter of pipe length.
Note on F15: Reference (maximal) heat losses for year-round operation (8760h) at design operating point